## Slide 1: Hybrid Energy Storage Application in Microgrid
Indian Institute of Technology Guwahati
Department of Energy Engineering
B.TECH PROJECT · FINAL PRESENTATION
Optimal cost sizing of a PV–battery–supercapacitor HESS for a DC microgrid
PRESENTED BY
Amit Raj
Roll No. [__]
UNDER THE GUIDANCE OF
Kuldeep Kumar
[Month 2026]
Notes: Introduce yourself and the project in one sentence: finding the cheapest mix of solar PV, battery and supercapacitor that keeps a DC microgrid reliable over 20 years.

## Slide 2: Outline of the talk
ROADMAP
01
Background
Microgrids, why they need storage, battery vs supercapacitor
02
Problem
Literature, research gap, objectives and system architecture
03
Data
IIT Guwahati solar resource, campus load and cost inputs
04
Methodology
Simulator, degradation, NPC, PSO and the XGBoost surrogate
05
Results
Cases A, B and C compared on cost, reliability and battery life
06
Conclusion
Key findings, limitations and future work
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
2 / 30
Notes: Walk through the six parts quickly; spend most of the time on methodology and results.

## Slide 3: What is a microgrid?
INTRODUCTION
A microgrid is a local group of generators, storage and loads that works as one controllable unit — connected to the main grid or running on its own (islanded).
Generation sits close to the load
Storage smooths supply–demand mismatch
A controller (EMS) dispatches every unit
Disconnects at the point of common coupling (PCC) during grid faults
Utility grid
PCC · static switch
Common bus (AC or DC)
Solar PV
Rooftop and ground arrays
Generators
Diesel, biogas, wind
Storage
Battery, supercapacitor
Loads
Hostels, labs, offices
Microgrid controller (EMS) — monitors and dispatches every unit
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
3 / 30
Notes: Define a microgrid: local sources, storage and loads acting as one unit behind a single connection point. A university campus like IIT Guwahati is a classic example. Storage is the part this project focuses on.

## Slide 4: Types of microgrids
INTRODUCTION
BUS TYPE
AC microgrid
Common AC bus; ties easily to the utility, but every DC source needs an inverter plus frequency and reactive-power control.
BUS TYPE
This project
DC microgrid
PV, batteries and supercapacitors are natively DC: fewer conversion stages, no frequency control — a natural fit for a HESS.
OPERATING MODE
Grid-connected
Exchanges power with the utility at the PCC; the grid absorbs any surplus or deficit.
OPERATING MODE
Islanded
Runs on its own; storage must cover every mismatch, so reliability becomes the design constraint.
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
4 / 30
Notes: Two ways to classify: by bus (AC or DC) and by operating mode. This work studies a DC microgrid where storage alone must meet the reliability target.

## Slide 5: Why a solar microgrid needs storage
MOTIVATION
Fig. — PV generation vs campus load on a typical day [insert your plot]
Daily mismatch
PV peaks at midday; the campus load stays high around the clock (load factor 0.82).
Fast fluctuations
Passing clouds and load steps cause second-scale swings that wear batteries out.
Reliability target
Unmet energy must stay within LPSP ≤ 1 % across a 20-year horizon.
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
5 / 30
Notes: Point at the figure: solar is a midday hump, load is nearly flat. Storage covers the hourly gap; fast fluctuations are a second, different problem — this sets up the case for two storage types.

## Slide 6: Battery vs supercapacitor
BACKGROUND
Property | Battery (lead-acid) | Supercapacitor
Energy density | High | Low
Power density | Moderate | Very high
Response time | Seconds to minutes | Milliseconds
Cycle life | Hundreds to a few thousand | Hundreds of thousands
Cost per kWh | Low | High
Best at | Bulk energy over hours | Short bursts and transients
Neither alone is cost-optimal: the battery handles energy, the supercapacitor handles power → combine them in a Hybrid Energy Storage System (HESS).
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
6 / 30
Notes: The two devices are complementary. Batteries store a lot of energy cheaply but suffer from frequent cycling; supercapacitors deliver fast power and survive huge numbers of cycles but are expensive per kWh.

## Slide 7: HESS: splitting power by frequency
BACKGROUND
Net power
P_net(t) = P_PV(t) − P_load(t)
Low-pass filter
Cut-off frequency f_c — a decision variable
Battery · slow part
P_bat = LPF{P_net}: energy-heavy swings
Supercapacitor · fast part
P_sc = P_net − P_bat: transients and spikes
Higher f_c
Battery sees more fluctuation; a smaller supercapacitor suffices.
Lower f_c
Battery is smoother and lasts longer; the supercapacitor must grow.
This work
Chooses f_c together with all component sizes for minimum cost.
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
7 / 30
Notes: The filter is the heart of a HESS. The cut-off frequency decides who does what — and therefore how big the supercapacitor must be and how hard the battery works. That trade-off is exactly what the optimiser explores.

## Slide 8: Related work
LITERATURE
Work | Approach | Storage | Gap for this project
Kumar et al., IEEE Access, 2018 | HOMER techno-financial study of the IITG campus | Lead-acid battery | No supercapacitor; no storage-type split
Thounthong et al., J. Power Sources, 2009 | Energy management of FC/battery/SC source for vehicles | Battery + SC | Control focus; not cost sizing
Kollimalla et al., IEEE Trans. Sust. Energy, 2014 | Control strategy for battery–SC storage | Battery + SC | Fixed split; cost not optimised
Etxeberria et al., IPEC, 2010 | Review of HESS for renewable integration in microgrids | Various | Survey; no site-specific sizing
This work extends Kumar et al. on the same campus: add a supercapacitor and co-optimise the power split with component sizes.
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
8 / 30
Notes: Kumar et al. is the anchor paper: same site, same department, battery-only storage in HOMER. The HESS papers are about control rather than lifetime cost. Verify volume/page details of the three HESS papers before the final version.

## Slide 9: Research gap and objectives
PROBLEM STATEMENT
Research gap
Campus microgrid studies size battery-only storage
HESS papers focus on control, not lifetime cost
The filter cut-off f_c is usually fixed, not optimised
Objectives
Build an hourly simulator of a PV–battery–SC DC microgrid for the IITG site
Model battery wear with rainflow cycle counting
Minimise 20-year Net Present Cost subject to LPSP ≤ 1 %
Co-optimise PV size, battery energy, SC strings and f_c; compare Cases A, B and C
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
9 / 30
Notes: State the gap in one breath, then the four objectives. Objective 4 — co-optimising the split frequency with the sizes — is the novel contribution.

## Slide 10: DC microgrid architecture
SYSTEM
Solar PV array
N_PV modules
Battery bank
E_bat (kWh), lead-acid
Supercapacitor
N_SC strings
Campus load
Hourly profile
DC–DC boost + MPPT
Bidirectional DC–DC
Bidirectional DC–DC
Load converter
Common DC bus · [__ V]
Energy management: low-pass filter (f_c) sets battery and SC references; unmet energy is logged to compute LPSP
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
10 / 30
Notes: Every unit connects to one DC bus through its own converter. The four sizing decisions are visible here: number of PV modules, battery energy, supercapacitor strings, and the filter cut-off inside the EMS. Fill in your bus voltage.

## Slide 11: Site and input data — IIT Guwahati
DATA
SOLAR RESOURCE · NASA POWER, 2023
1,639
kWh/m² annual irradiation
964
W/m² peak GHI
4,149
daylight hours per year
23.4 °C
mean ambient temperature
CAMPUS LOAD · KUMAR ET AL., 2018
60,379
kWh/day energy demand
3,075
kW peak load
2,516
kW average load
0.82
load factor
Site 26.19° N, 91.70° E · 285 ha campus · load and solar from the same region · [load scaled to __ kW in this study]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
11 / 30
Notes: Solar data are hourly GHI and 2 m temperature from NASA POWER for 2023. The load shape is digitised from Fig. 5 of Kumar et al. Both come from the same location, which is why other public load datasets were rejected. Mention any scaling you applied.

## Slide 12: Input profiles
DATA
Fig. 1 — Hourly GHI and ambient temperature, Guwahati 2023 (NASA POWER)
Fig. 2 — Campus hourly load profile (digitised from Kumar et al., Fig. 5)
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
12 / 30
Notes: Show the two raw inputs the simulator consumes. A heatmap (hour vs day of year) works well for GHI if you have it.

## Slide 13: Component and cost parameters
DATA
Component | Capital cost | O&M | Key parameters
Solar PV (fixed axis) | Rs 50,502 / kW | Rs 700 / kW·yr | CERC all-in cost
Lead-acid battery, 12 V 3 kWh | Rs 22,000 / unit (≈ Rs 7,333 / kWh) | Rs 700 / unit·yr | RTE 85 %, min SoC 20 %
Bidirectional converter | Rs 10,000 / kW | — | —
Supercapacitor module | [Rs __ / module] | [Rs __ / yr] | [Part no., F, V, ESR]
Replacement cost = capital cost · Real discount rate 4.72 % = 1.1070 / 1.0571 − 1 · Horizon 20 years · Source: CERC (2016) via Kumar et al. (2018)
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
13 / 30
Notes: All PV, battery and converter costs trace to CERC 2016 as used in Kumar et al. The real discount rate removes inflation because cash flows are in constant rupees. Fill in the supercapacitor datasheet and price.

## Slide 14: Four-stage sizing pipeline
METHODOLOGY
01
Hourly simulator
8,760-hour energy balance; outputs LPSP and SoC trace
02
Rainflow degradation
Battery cycles by depth of discharge → replacements and cost
03
LHS + XGBoost
Latin Hypercube samples train a fast surrogate of NPC and LPSP
04
PSO optimiser
Minimum-NPC search, benchmarked against a coarse grid search
THREE COMPARISON CASES
Case A
Battery only — baseline
Case B
Hybrid, fixed power split
Case C · novel
Hybrid, co-optimised split
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
14 / 30
Notes: The simulator is the foundation: think of it as a function from a design to its cost and reliability. XGBoost is only there for speed. PSO searches the design space; the grid search checks that PSO finds the right answer.

## Slide 15: Hourly simulator: energy balance
METHODOLOGY · STAGE 1
PV output
P_PV(t) = N_PV · P_STC · (G(t) / 1000) · [1 + α_T (T_c(t) − 25)] · η_der
Net power
P_net(t) = P_PV(t) − P_load(t)
Battery state of charge
SoC(t+1) = SoC(t) + η · P_bat(t) · Δt / E_bat, 20 % ≤ SoC ≤ 100 %
Reliability
LPSP = Σ E_unmet(t) / Σ E_load(t) ≤ 1 %
Dispatch each hour
Surplus: charge the battery up to its limit, then spill
Deficit: discharge the battery down to 20 % SoC
Any remaining deficit is logged as unmet energy
Δt = 1 h over 8,760 h; outputs feed the degradation and cost models
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
15 / 30
Notes: Edit the equations to match exactly what your simulator implements (derating, temperature model, charge/discharge efficiencies). The simulator is a function: give it a design, it returns LPSP and the SoC trace.

## Slide 16: Supercapacitor sizing across timescales
METHODOLOGY
The problem
An hourly step averages away the second-scale transients a supercapacitor exists to absorb.
The fix: analytical sizing
E_SC = ½ C (V_max² − V_min²) ≥ ∫ P_SC(t) dt over the worst-case transient
N_SC strings follow from module energy and the DC-bus voltage.
The link back
A larger SC strips fast stress from the battery → fewer micro-cycles in the rainflow model → longer battery life.
Fig. — Worst-case transient event and resulting SC power profile [insert your plot]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
16 / 30
Notes: This is the timescale mismatch you resolved: hourly data cannot see transients, so the SC is sized analytically from a worst-case event, and its benefit enters the cost model through reduced battery wear.

## Slide 17: Battery degradation via rainflow counting
METHODOLOGY · STAGE 2
Take the SoC trace from the simulator
Rainflow counting (ASTM E1049) extracts each cycle and its depth of discharge
Look up cycle life N(DoD) from the battery datasheet curve
Accumulate damage with Miner’s rule; replace the battery when D reaches 1
D = Σ nᵢ / N(DoDᵢ)
Replacements per 20 years feed directly into NPC.
Fig. — Rainflow cycle histogram: cycle count vs depth of discharge [insert your plot]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
17 / 30
Notes: Deep cycles hurt far more than shallow ones; rainflow counting captures that from an irregular SoC signal. Mention the cycle-life data source you used for the lead-acid battery.

## Slide 18: Economic model: Net Present Cost
METHODOLOGY
OBJECTIVE
NPC = Σₖ [ C_cap,k + Σₜ (C_O&M,k(t) + C_rep,k(t)) / (1 + r)ᵗ − S_k / (1 + r)ᴺ ]
k = PV, battery, SC, converters · C_rep from rainflow-driven replacements · S_k = salvage value · N = 20 years
Real discount rate
r = 1.1070 / 1.0571 − 1 = 4.72 %
Capital recovery
CRF = r(1 + r)ᴺ / ((1 + r)ᴺ − 1)
Levelised cost
LCOE = NPC · CRF / annual energy served
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
18 / 30
Notes: Nominal discount 10.70 % and inflation 5.71 % from CERC give a real rate of 4.72 %, used because all costs are in constant rupees. NPC is the single number the optimiser minimises.

## Slide 19: Optimisation problem and PSO
METHODOLOGY · STAGE 4
x = [N_PV, E_bat, N_SC, f_c]
minimise NPC(x)
subject to LPSP(x) ≤ 1 %, x_min ≤ x ≤ x_max
Variable | Lower | Upper | Unit
N_PV | [__] | [__] | modules
E_bat | [__] | [__] | kWh
N_SC | [__] | [__] | strings
f_c | [__] | [__] | [Hz]
Particle Swarm Optimisation
Swarm [__] particles · [__] iterations · w = [__], c₁ = c₂ = [__]
LPSP violation handled by a penalty on NPC [confirm]
Benchmark
Coarse grid search over the same bounds — PSO must reach its best NPC with far fewer evaluations.
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
19 / 30
Notes: Four decision variables, one objective, one reliability constraint. Fill in your bounds and PSO settings. The grid search is the trust check for PSO.

## Slide 20: Surrogate model: LHS + XGBoost
METHODOLOGY · STAGE 3
[__]
LHS training samples
[__]
R² on test set (NPC)
[__]×
faster than simulator
Fig. — Parity plot: predicted vs simulated NPC
Fig. — Parity plot: predicted vs simulated LPSP
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
20 / 30
Notes: Frame XGBoost as a speed tool, not an accuracy upgrade: the simulator is the ground truth, and the final optimum is always re-checked with the simulator.

## Slide 21: Simulator verification
RESULTS
Fig. — One sample week: PV, load, battery power and SoC [insert your plot]
Sanity checks passed
Energy balance closes every hour
SoC stays within 20–100 %
Annual PV yield consistent with irradiation
LPSP falls as storage grows
[Add your own check]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
21 / 30
Notes: Before trusting any optimum, show the simulator behaves physically. Replace the checks listed with the exact ones you ran.

## Slide 22: Optimal designs: Case A vs B vs C
RESULTS
Case | PV (kW) | Battery (kWh) | SC strings | f_c | LPSP (%) | NPC (Rs M) | LCOE (Rs/kWh) | Battery life (yr)
A · Battery only | [__] | [__] | — | — | [__] | [__] | [__] | [__]
B · Hybrid, fixed split | [__] | [__] | [__] | [fixed] | [__] | [__] | [__] | [__]
C · Hybrid, co-optimised | [__] | [__] | [__] | [__] | [__] | [__] | [__] | [__]
[−__ %]
NPC, Case C vs Case A
[+__ yr]
Battery life gain, Case C vs A
[−__ %]
NPC, Case C vs Case B
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
22 / 30
Notes: This is the headline comparison. All three cases meet LPSP ≤ 1 %; the question is which does it most cheaply. Sanity-check NPC/LCOE against Kumar et al.’s off-grid range (LCOE about 12–18 Rs/kWh) if your system is islanded.

## Slide 23: Optimiser performance: grid search vs PSO
RESULTS
Fig. — NPC landscape from coarse grid search (PV size vs battery energy), infeasible region shaded
Observation: [__]
Fig. — PSO convergence: best NPC vs iteration, grid-search optimum as a dashed line
Observation: [__]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
23 / 30
Notes: Show that PSO lands on (or below) the grid-search optimum, and how many evaluations each needed.

## Slide 24: Power split in action
RESULTS
Fig. — Battery vs supercapacitor power during the worst-case transient
Observation: [__]
Fig. — Battery SoC over a typical week, Case A vs Case C
Observation: [__]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
24 / 30
Notes: Left: the supercapacitor absorbs the spike while battery power stays smooth. Right: a smoother SoC trace in Case C means fewer, shallower cycles.

## Slide 25: Battery stress and lifetime
RESULTS
Fig. — Rainflow cycle histograms, Case A vs Case C
Observation: [__]
Fig. — Cumulative battery damage D over 20 years, with replacement points
Observation: [__]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
25 / 30
Notes: This is where the supercapacitor pays for itself: fewer cycles, later replacements, lower replacement cost in NPC.

## Slide 26: Cost breakdown and sensitivity
RESULTS
Fig. — NPC breakdown by component (capital, O&M, replacement) for Cases A, B, C
Observation: [__]
Fig. — NPC and battery life vs cut-off frequency f_c (or vs SC price)
Observation: [__]
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
26 / 30
Notes: Where does the money go, and how robust is the optimum? A U-shaped NPC curve over f_c is the visual proof that co-optimising the split matters.

## Slide 27: Co-optimising the power split cuts NPC by [__] % versus battery-only storage
KEY RESULT
…while extending battery life from [__] to [__] years, at the same LPSP ≤ 1 % reliability.
Notes: Pause here. This one sentence is what the panel should remember. Replace the brackets with your Case A vs Case C numbers.

## Slide 28: Conclusions and future work
CONCLUSION
Conclusions
A PV–battery–SC DC microgrid for the IITG site was sized for minimum 20-year NPC at LPSP ≤ 1 %
Case C (co-optimised f_c) achieved [__]
Supercapacitors cut battery cycling stress by [__] %, delaying replacements
The XGBoost surrogate sped up evaluation by [__]× with R² of [__]
Future work
Sub-hourly simulation to capture transients directly
Adaptive, real-time power-split control
Li-ion chemistry and grid-connected scenarios
Hardware prototype or hardware-in-the-loop validation
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
28 / 30
Notes: Close with what was achieved and an honest scope note: no hardware in this 10-week project, so control and hardware validation are natural next steps.

## Slide 29: References
BIBLIOGRAPHY
[1] A. Kumar, A. R. Singh, Y. Deng, X. He, P. Kumar, R. C. Bansal, “Multiyear load growth based techno-financial evaluation of a microgrid for an academic institution,” IEEE Access, vol. 6, pp. 37533–37555, 2018.
[2] CERC, “Determination of levellised generic tariff for FY 2016-17,” Central Electricity Regulatory Commission, New Delhi, 2016.
[3] NASA Langley Research Center, POWER Project hourly data (GHI, T2M), accessed [date].
[4] P. Thounthong, S. Raël, B. Davat, “Energy management of fuel cell/battery/supercapacitor hybrid power source for vehicle applications,” J. Power Sources, 2009.
[5] S. K. Kollimalla, M. K. Mishra, N. L. Narasamma, “Design and analysis of novel control strategy for battery and supercapacitor storage system,” IEEE Trans. Sustain. Energy, 2014.
[6] A. Etxeberria, I. Vechiu, H. Camblong, J. M. Vinassa, “Hybrid energy storage systems for renewable energy sources integration in microgrids: a review,” IPEC, 2010.
[7] ASTM E1049-85, Standard practices for cycle counting in fatigue analysis.
[8] J. Kennedy, R. Eberhart, “Particle swarm optimization,” Proc. IEEE ICNN, 1995.
[9] T. Chen, C. Guestrin, “XGBoost: a scalable tree boosting system,” Proc. ACM SIGKDD, 2016.
[10] M. D. McKay, R. J. Beckman, W. J. Conover, “A comparison of three methods for selecting values of input variables in the analysis of output from a computer code,” Technometrics, 1979.
Amit Raj · Hybrid Energy Storage Application in Microgrid · B.Tech Project, IIT Guwahati
29 / 30
Notes: Verify volume, issue and page numbers for [4]–[6] on IEEE Xplore or the publisher site before presenting.

## Slide 30: Thank you
Indian Institute of Technology Guwahati
Questions and discussion
Amit Raj · Supervisor: Kuldeep Kumar · Energy Engineering, IIT Guwahati
Notes: Invite questions. Likely ones: why lead-acid not Li-ion, how the SC was priced, how the worst-case transient was chosen, and how accurate the surrogate is.