## Slide 1
B.TECH PROJECT — PROGRESS REVIEW
Optimal Sizing of a PV–Battery–
Supercapacitor Hybrid Storage
System for a Campus Microgrid
Site data, a validated bottom-up load model, a verified simulator, and a first optimal design for IIT Guwahati.
PRESENTED BY
Amit Raj
Energy Engineering
SUPERVISOR
Kuldeep Kumar
INSTITUTE
IIT Guwahati
2026 – 27
Notes: Open with the one-line problem: cheapest set of PV, battery and supercapacitor sizes that still meets the load for this campus.

## Slide 2
THE PROBLEM
Cheapest system that still keeps the lights on
02
Decision variables
PV capacity (kW), battery strings, supercapacitor strings.
Objective
Minimise Net Present Cost over the project life: capital, replacements and O&M, discounted.
Constraint
LPSP ≤ 1 % — at most 1 % of demanded energy may go unserved. Without it, the cheapest system is no system.
Three optimisation stages, each checked against the one before
1
Grid search
DONE
Exhaustive sweep. Slow but honest — the benchmark.
2
Particle Swarm
NEXT
Same answer with far fewer simulator calls.
3
XGBoost surrogate
PLANNED
Predicts cost and reliability; becomes necessary at sub-hourly resolution.

## Slide 3
DATA
Site and data sources
03
Solar resource — NASA POWER
Hourly irradiance and temperature for 26.19° N, 91.69° E. Satellite-derived on a 0.5° grid — about a 50 km cell, so regional rather than rooftop-specific.
1,639
kWh/m² per year
964
W/m² peak GHI
4,149
daylight hours
23.4 °C
mean temperature
Load reference — Kumar et al., IEEE Access 2018
A HOMER microgrid study of this exact campus, co-authored by IIT Guwahati faculty. Reports the campus statistics our model is validated against:
3,075 kW
peak
2,515.8 kW
average
0.82
load factor
Considered and rejected
ELMAS, Fluvius/MODERATE and NREL ResStock load sets. Pairing foreign demand with Guwahati solar creates a seasonal correlation that exists nowhere.

## Slide 4
LOAD MODEL
Built department by department — and validated
04
13 departments and facilities
Each with a floor-area load, a continuous base load, and an explicit equipment list — plus Guwahati seasonality and the academic calendar.
Mech + Central Workshop
CNC, EDM, welding, foundry
EEE
M-G sets, PE benches, HV test set
Chemistry / Chem Engg
fume hoods, furnaces, pilot plant
Physics / Biosciences
cryostats, cold rooms, autoclaves
CSE / Central Instruments
HPC cluster, NMR, SEM
Hostels and services
pumping, mess, street lighting
Bottom-up model vs published campus figures
Chart: 
| Mean demand (kW) | Peak demand (kW)
Bottom-up model | 2524 | 3411
Published (Kumar et al.) | 2515.8 | 3075
0.3 %
gap on mean demand — never fitted to it. Peak runs 11 % high and load factor 0.74 vs 0.82, so the model is slightly peakier than the real campus.

## Slide 5
SCOPE AND THE TRANSIENT PROBLEM
What we size, and why an hourly model can’t see a supercapacitor
05
System modelled
Mech + Central Workshop and EEE, at true machine ratings. Scaling the whole campus down would shrink a 35 kW furnace to 2 kW.
644 kW
peak demand
3.27 GWh
annual demand
0.579
load factor
A supercapacitor discharges in seconds. At hourly resolution it has no visible effect, so an optimiser sizes it to zero. The transient is therefore carried as a separate design parameter, from the worst credible coincident switching:
Chart: 
| Foundry furnace | HV test set | CNC milling | CNC lathe
Step (kW) | 35 | 25 | 18 | 15
93 kW
for 5 seconds
465 kJ
energy to absorb
4 strings
24 modules each, 380 V bus

## Slide 6
COST MODEL
Every rupee traces to one source
06
Kumar et al., Table 2 and Section IV-C — which rest on the CERC benchmark tariff order for FY 2016-17.
Solar PV
₹50,502 / kW
All-in per CERC: modules, civil works, mounting, inverter, evacuation. ₹700/kW/yr O&M.
Battery
₹7,333 / kWh
Discover 12VRE-3000TF-L lead-acid, ₹22,000 per 3 kWh unit. 85 % round trip, SoC 20–100 %.
Converter
₹10,000 / kW
Bidirectional, zero O&M.
Economics
15 years
Fixed O&M ₹500,000/yr. Grid tariff ₹5.96/kWh.
CORRECTION APPLIED
4.72 %
real discount rate = (1.1070 / 1.0571) − 1. The paper’s 10.70 % is nominal; using it on constant-rupee cash flows makes a year-10 battery replacement look ~40 % cheaper, biasing the design toward undersized storage.
Not in the paper — placeholders until sourced: supercapacitor module price, battery lifetime throughput, PV derating and temperature coefficient.

## Slide 7
SIMULATOR
One function, verified before trusted
07
simulate(pv_kw, batt_strings, sc_strings)
→ NPC, LPSP, score
1
PV output from the paper’s eq. (3), NOCT cell temperature
2
8,760-hour dispatch tracking battery state of charge
3
Unmet energy → LPSP; surplus beyond capacity → curtailment
4
Throughput → battery life → replacements → NPC
5
Constraints folded into one penalised score for the optimiser
6.7 ms per evaluation
A wrong simulator returns plausible numbers, not errors. Seven checks run on every execution:
PASS
No PV, no battery → LPSP = 1.000
PASS
Huge system → LPSP = 0
PASS
Doubling PV lowers LPSP
PASS
Doubling PV raises NPC
PASS
SoC never leaves its limits
PASS
Annual energy balance closes to 0.00 %
PASS
Undersized SC bank is penalised

## Slide 8
FIRST RESULT
Cheapest design meeting LPSP ≤ 1 %
08
Grid sweep of 300 designs — 150 feasible.
3,500 kW
PV
16,800 kWh
battery · 280 strings
4 strings
supercapacitor
0.90 %
LPSP
₹467.6 M
net present cost
₹9.63 / kWh
LCOE
Benchmark: the paper reports ₹11.96–18.47/kWh off-grid for the whole campus. Ours is lower and explicably so — two departments, no diesel, no biogas, no 10 % load growth.
Boundary check: optimum is interior on both axes — not a grid artefact.

## Slide 9
PHYSICAL FINDING
The battery is sized by four cloudy days, not by season
09
Monthly energy surplus at the optimum (MWh) — every month positive
Chart: 
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Surplus (MWh) | 74 | 62 | 108 | 161 | 178 | 106 | 132 | 41 | 102 | 79 | 95 | 77
WORST DEFICIT RUN
4 days
from 21 August · 16,384 kWh short
BATTERY CHOSEN
13,440 kWh
usable · 1.5 days of autonomy
The optimiser covered 82 % of the worst event on its own. Covering the last 18 % costs more than the reliability it buys.

## Slide 10
TRADE-OFF
Generation and storage substitute almost freely
10
Net present cost of the five cheapest feasible designs (₹ million)
Chart: 
| 3.5 MW / 16.8 MWh | 4.0 MW / 15.6 MWh | 4.0 MW / 12.0 MWh | 3.5 MW / 18.0 MWh | 5.0 MW / 7.2 MWh
NPC | 467.6 | 480.8 | 482.4 | 482.9 | 489.9
4.8 %
cost spread across designs spanning 3.5–5.0 MW of PV and 7.2–18.0 MWh of battery.
What follows
A flat basin, not a sharp optimum — prices will move the answer, so sensitivity is a headline result.
Well suited to PSO and a Pareto-front view.

## Slide 11
HONEST POSITION
Limitations, and the next phase
11
Limitations
Placeholders
SC price, battery throughput, PV derating. Battery throughput drives replacements — the most consequential.
Estimated ratings
Machines are real; their kW figures are engineering estimates, not nameplate.
Hourly resolution
No power split is modelled — the supercapacitor is a cost and a constraint, not a simulated device.
NEXT: ONE-MINUTE RESOLUTION
1
Supercapacitor becomes a simulated device against real transients
2
Low-pass filter cut-off becomes a decision variable
3
Battery current stress becomes observable — rainflow on real cycles
4
Fixed vs co-optimised split becomes a measurement, not a claim
Simulator cost rises from 6.7 ms to ~0.4 s — the point where the surrogate becomes necessary. The hourly model stays: it sizes energy, sub-hourly sizes power.

## Slide 12
THREE REQUESTS
What would unblock the next phase
1
Battery cycle-life data
Discover 12VRE-3000TF-L cycles at two depths of discharge — or approval to switch the study to lithium-ion.
2
Central Workshop access
To record nameplate ratings for the CNC machines, welding sets and foundry furnace.
3
Agreement on direction
Sign-off on the one-minute resolution phase before a week is committed to it.
Reference: A. Kumar et al., “Multiyear Load Growth Based Techno-Financial Evaluation of a Microgrid for an Academic Institution,” IEEE Access, vol. 6, pp. 37533–37555, 2018.